Standard test on UPS

This assumes the ups is hooked up to a CPDlive system (although it would also work if it wasn’t.)

Open a terminal window

Start an eavesdropper session by typing:

evs

adjust parameters in the eavesdropper session by using up/down arrows and space bar.

(highlight ‘exclusive’ so CPDlive doesn’t get confused

(highlight ‘log traffic to disc’

(switch port id to the port that the UPS is attached to (use back space)

To apply changes type:

<esc>

It should start logging data – and showing data on the eavesdropper screen (approx. every 15 sec).

In the eavesdropper logging screen type a series of commands to get the information you want logged:

pw 2639    	(this is the factory level password)

pr 79 1		(takes out of unpolled mode)

s		(status command)

p 0 139	(display ups parameters from 0 to 139)

Use menu at bottom to bring evs window again

(turn off exclusive

(turn off log traffic to disc

<esc>  apply changes

In the eavesdropper logging screen type a series of commands to get the UPS back to the desired setting:

pr 79 4		(starts unpolled)

pw		(clears password)

quits evs:

<control><c>

In cpd root directory /home/cpd/ there should be a log file called by the port name, e.g., ‘ttyUSB4.log’.  Copy this file to vortex directory /aer/doc/inst/ups/ser#_stn_date

ser# is the UPS serial number

stn is the station the UPS is at when the test is done

date is the date of the test